## Slide 1: Cyclone Mxi Product Details

## Slide 2: Tank Construction
Exhaust/condensate relocated to front
T&P relocated to left side
Addition of recirculation loop return opening
Larger diameter combustion tube
  150 – 250 was 5” now 6”
  300 – 500 was 8” now 10” (new 119 gal capacity)
Fire tube cone transition
Additional row of coil

## Slide 3: Exhaust/Condensate Elbow
Aluminum Condensate Elbow
  Water trap
  Debris trap and cleanout
  Threaded port for condensate drain
  Blocked outlet switch connection

## Slide 4: Top Components
Enable/Disable switch
Pressure switches vertically mounted
Pressure switches grouped (from the front)
  Blocked outlet with red label
  Blocked inlet with aqua label
  Blower prover with red label
Honeywell spark module
New design control box
Field wiring junction box

## Slide 5: 120 Model Combustion System
EBM RG128 Blower
Honeywell VK8115FB Natural Gas Valve/Venturi Assy with 053 Venturi
Honeywell VK8115F LP Gas Valve/Venturi Assy with 003 Venturi
Acunit Burner
Kanthal APM Spark Electrode
  .125” Spark Gap (between spark rod and ground rod)
  ¼” – 5/16” away from burner surface
Kanthal APM Flame Rod
  ½” away from burner surface
Aluminum Burner/Blower Adaptor

## Slide 6: 150 – 250 Models Combustion System
EBM RG148 Enhanced Blower
Honeywell VK8115FB Natural Gas Valve/Venturi Assy with 052 Venturi
Honeywell VK8115F LP Gas Valve/Venturi Assy with 052 Venturi
Acunit Burner
Kanthal APM Spark Electrode
  .125” Spark Gap (between spark rod and ground rod)
  ¼” – 5/16” away from burner surface
Kanthal APM Flame Rod
  ½” away from burner surface
Aluminum Burner/Blower Adaptor
Burner Plate 6-Bolt Hole Pattern
409 SS Heat Shield

## Slide 7: 300 – 500 Models Combustion System
Fasco Blower w/Hall Effect Sensor (RPM feed back). Smaller blower foot
Dung’s Gas Valve
New Venturi Insert (Grey)
70mm Acunit Burner
409 SS Heat Shield
1” Pyrolite Insulation Block
Heat Shield and Insulation Block (bolted to the Burner Plate w/SS bolts and spacers)
Burner Plate 8-Bolt Hole Pattern
Kanthal APM Spark Electrode (different bend then 120-250)
  .125” Spark Gap (between spark rod and ground rod)
  ¼” – 5/16” away from burner surface
Kanthal APM Flame Rod (Longer Ceramic) and Bent away from Burner
    ¾” away from burner surface

## Slide 8: Key Marketing Features
Modulation benefits
  Increased efficiency at lower firing rates
  Fewer cycles result in longer service life
  Quieter operation at lower fire rates
Modulation details
  Modulates when within 30 degrees of set point
  Input lowers closer to set point
  Up to 3:1 modulation from largest model in family (120, 250, 500)

## Slide 9: Modulation Details Continued…
Utilizes PID algorithm
Proportional
  30°F proportional band
    Full fire if temperature is >30°F below setpoint
    Proportional to difference
      Full fire at 30°F
      Minimum rate fire at set point
Integral
  Adds more speed the longer below set point
  Subtracts speed the longer above set point
Differential
  Looks ahead with rapid changes to adjust output

## Slide 10: Modulation Details Continued…
After 8 min of continuous operation unit accelerates to full fire/RPM for 45 seconds
All blowers have RPM feedback back to controller
  3 model families (120, 150-250,300-500) all have same pre-purge, ignition and post ignition RPM’s
Thermostat differential remains factory set at 8 degrees
Tank temp remains 12:1 upper probe to lower probe

## Slide 11: Venting
  3” & 4” vent size for 120 – 250 (Same as current models)
  4” & 6” vent size for 300 – 500 (Same as current models)
Same max. equivalent vent length as current production
PVC, CPVC, PP, AL29-4C Vent Materials
  ULC S636 Approved
  Approved Polypropylene- M&G Duravent and Centrotherm InnoFlue
  Approved AL29-4C are HeatFab Saf-T and Duravent FasNSeal

## Slide 12: Venting
  Vents lengths unchanged
  Vent terminations
  Standard termination (45 degree intake and 45 degree exhaust)
  Concentric venting termination (Optional)
    120 to 250 use 3” concentric
    300 to 500 use 4” concentric
  Low profile venting termination (Optional)
    3 & 4” options

## Slide 13: New Control Box
Power Supply
Low Voltage Field Wiring. CCB
Transformer
Configuration Key

## Slide 14: New Control Sequence of Operation
Simplified Sequence
  Call for heat
    Pre-purge
    Slow down blower and start spark
    Wait for blower to stabilize
    Turn on gas valve
    Wait for flame signal
    Ramp up to post ignition speed and wait
    Ramp down to heating speed (or modulation)
  End Call for heat
    Post-purge speed
    Standby

## Slide 15: Powered Anode
Algorithm to adapt setpoint to low conductivity
Calibration checks of hardware and tank on power up and just under every two hours
New probe improvements to eliminate shorting at spud
Higher currents (up to 175mA)
Notes: Have a separate presentation for powered anode.

## Slide 16: Model Families
120 Model
  Max modulation down to 78,000 Btu/h
  Single anode
150 - 250 Models
  Max modulation down to 78,000 Btu/h
  Common parts on 150 – 250 models
300 – 500 Models
  Max modulation down to 195,000 Btu/h
  VFD (variable frequency drive)
  Common parts on 300 – 500 models

## Slide 17: Thinks to Know
Replacements will require vent realignment
Blower ramps up/down
Blower sound at high RPM with no intake
300 – 500 models are all 119 gallon now
300 model requires larger 4” concentric now
300-500 models are ¼” taller
High altitude up to 10,100 ft
We will market Modulation and its benefits but not publish 3:1 modulation rates

## Slide 18: Rated Thermal Efficiencies
Model Size | Series 100 | New Series 200
120 | 94% | 95%
150 | 95% | 98%
199 | 95% | 97%
250 | 95% | 96%
300 | 96% | 96%
400 | 95% | 95%
500 | 95% | 95%

## Slide 19: Reliability Improvements
Change to spark ignition
Modulation (fewer cycles and less thermal stress)
New vertically mounted pressure switches
Larger diameter fire tube (150 – 500 models)
Fire tube cone transition
Improved condensate drain
Powered anode enhancements
Improved low gas operation
Smoother light off

## Slide 20: New/Enhanced Features
Modulation
Increased efficiency
Easy access exhaust and condensate
New vent material options
New low profile vent termination kits
Addition of recirculation loop return connection
Common parts

## Slide 21: Summary
The best just got better, the bar has been raised again
New Series 200/201
No price increase related to these improvements
All model sizes released and ready for order

## Slide 22: Cyclone Mxi Summary
Combination of feature and reliability improvements
Model numbers remain the same, new Series 200
No price increase related to these improvements
June 18th is order transition date